## CALCULATOR
[7 empty] | Panduit Patch Cord Approximate Diameters | [5 empty] | Cat 6A Plenum UTP Cable | Dia. (in.)
[13 empty] | Panduit Vari-MaTriX HD | 0.23
[7 empty] | Cat. | AWG | in. |  | mm |  | Panduit Std Comp+ HD | 0.23
[7 empty] | 5e | 28 | 0.149 |  | 3.7846 |  | CommScope 2091B | 0.285
[7 empty] | 5e | 24 | 0.215 |  | 5.461 |  | CommScope 2091SD | 0.265
[7 empty] | 6 | 28 | 0.15 |  | 3.81 |  | Belden 10GXS | 0.265
Enter the cable diameter below and select in. or mm. | [6 empty] | 6 | 24 | 0.235 |  | 5.969 |  | Berk-Tek LANmark-XTP | 0.275
[7 empty] | 6A | 28 | 0.185 |  | 4.699
Cable Diameter = | 0.25 | 1 |  |  |  |  | 6A | 24 | 0.25 |  | 6.35
| Duplex Cable? | 1
Product Family | Part Number | Description | Cable Manager Area |  |  | Recommended Cable Fill (30%) |  |  |  | Maximum Cable Fill (50%)
|  |  | Front Usable Area (sq. in.) | Rear Usable Area (sq. in.) | Total Usable Area (sq. in.) | Front | Rear | Total |  | Front | Rear | Total
PR2V PatchRunner™ 2 Vertical Cable Managers | PR2VD06 | 6" wide | 45.11 | 27.26 | 72.37 | 275 | 166 | 442 |  | 459 | 277 | 737
| PR2VFD06 | 6" wide, front only | 45.11 | 0 | 45.11 | 275 | 0 | 275 |  | 459 | 0 | 459
| PR2VD08 | 8" wide | 63.71 | 39.73 | 103.44 | 389 | 242 | 632 |  | 648 | 404 | 1053
| PR2VFD08 | 8" wide, front only | 63.71 | 0 | 63.71 | 389 | 0 | 389 |  | 648 | 0 | 648
| PR2VD10 | 10" wide | 82.31 | 52.21 | 134.52 | 503 | 319 | 822 |  | 838 | 531 | 1370
| PR2VFD10 | 10" wide, front only | 82.31 | 0 | 82.31 | 503 | 0 | 503 |  | 838 | 0 | 838
| PR2VD12 | 12" wide | 100.9 | 64.68 | 165.58 | 616 | 395 | 1011 |  | 1027 | 658 | 1686
| PR2VFD12 | 12" wide, front only | 100.9 | 0 | 100.9 | 616 | 0 | 616 |  | 1027 | 0 | 1027
| Single PR2V Finger |  |  |  | 5.8 | 35 |  |  |  | 59
PR2VRG PatchRunner™2 Rear Gate Accessory | PR2VRGSK06 | 6" wide gate kit | 0 | 43.45 | 43.45 | 0 | 265 | 265 |  | 0 | 442 | 442
| PR2VRGSK08 | 8" wide gate kit | 0 | 59.51 | 59.51 | 0 | 363 | 363 |  | 0 | 606 | 606
| PR2VRGSK10 | 10" wide gate kit | 0 | 75.57 | 75.57 | 0 | 461 | 461 |  | 0 | 769 | 769
| PR2VRGSK12 | 12" wide gate kit | 0 | 91.63 | 91.63 | 0 | 560 | 560 |  | 0 | 933 | 933
PR2HF PatchRunner™2 Horizontal Cable Managers | PR2HF1 | 1RU, front only | 5.1 | 0 | 5.1 | 31 | 0 | 31 |  | 51 | 0 | 51
| PR2HF2 | 2RU, front only | 12.5639 | 0 | 12.5639 | 76 | 0 | 76 |  | 127 | 0 | 127
| PR2HF3 | 3RU, front only | 23.0956 | 0 | 23.0956 | 141 | 0 | 141 |  | 235 | 0 | 235
| PR2HF4 | 4RU, front only | 33.6272 | 0 | 33.6272 | 205 | 0 | 205 |  | 342 | 0 | 342
PE2V PatchRunner™ 2 High Capacity Vertical Cable Managers | PE2VD06 | 6" wide | 66.1018 | 44.2782 | 110.38 | 403 | 270 | 674 |  | 673 | 451 | 1124
| PE2VFD06 | 6" wide, front only | 66.1018 | 0 | 66.1018 | 403 | 0 | 403 |  | 673 | 0 | 673
| PE2VD08 | 8" wide | 92.4809 | 63.0973 | 155.5782 | 565 | 385 | 950 |  | 942 | 642 | 1584
| PE2VFD08 | 8" wide, front only | 92.4809 | 0 | 92.4809 | 565 | 0 | 565 |  | 942 | 0 | 942
| PE2VD10 | 10" wide | 118.8599 | 81.9639 | 200.8238 | 726 | 500 | 1227 |  | 1210 | 834 | 2045
| PE2VFD10 | 10" wide, front only | 118.8599 | 0 | 118.8599 | 726 | 0 | 726 |  | 1210 | 0 | 1210
| PE2VD12 | 12" wide | 145.239 | 100.7355 | 245.9745 | 887 | 615 | 1503 |  | 1479 | 1026 | 2505
| PE2VFD12 | 12" wide, front only | 145.239 | 0 | 145.239 | 887 | 0 | 887 |  | 1479 | 0 | 1479
| Single PE2V Finger |  |  |  | 5.8 | 35 |  |  |  | 59
WMPV NetRunner™ Vertical Cable Managers | WMPV22E | 4.9" wide, 22RU | 17.3 | 17.3 | 34.6 | 105 | 105 | 211 |  | 176 | 176 | 352
| WMPVF22E | 4.9" wide, 22RU, front only | 17.3 | 0 | 17.3 | 105 | 0 | 105 |  | 176 | 0 | 176
| WMPV45E | 4.9" wide, 45RU | 17.3 | 17.3 | 34.6 | 105 | 105 | 211 |  | 176 | 176 | 352
| WMPVF45E | 4.9" wide, 45RU, front only | 17.3 | 0 | 17.3 | 105 | 0 | 105 |  | 176 | 0 | 176
| WMPVHC45E | 6.7" wide, 45RU | 30.7 | 30.7 | 61.4 | 187 | 187 | 375 |  | 312 | 312 | 625
| WMPVHCF45E | 6.7" wide, 45RU, front only | 30.7 | 0 | 30.7 | 187 | 0 | 187 |  | 312 | 0 | 312
| Single WMPV Finger |  |  |  | 3.7 | 22 |  |  |  | 37
| Single WMPVHC Finger |  |  |  | 4.7 | 28 |  |  |  | 47
WMP PatchLink™ Horizontal Cable Managers | WMP1E | 2RU, front/rear | 7.6 | 10.6 | 18.2 | 46 | 64 | 111 |  | 77 | 107 | 185
| WMPF1E | 2RU, front only | 7.6 | 0 | 7.6 | 46 | 0 | 46 |  | 77 | 0 | 77
| WMPH2E | 2RU, front/rear, w/ bend rad. clips | 5.9 | 10.6 | 16.5 | 36 | 64 | 100 |  | 60 | 107 | 168
| WMPHF2E | 2RU, front only, w/ bend rad. clips | 5.9 | 0 | 5.9 | 36 | 0 | 36 |  | 60 | 0 | 60
| WMPSE | 1RU, front/rear | 3.5 | 6.3 | 9.8 | 21 | 38 | 59 |  | 35 | 64 | 99
| WMPFSE | 1RU, front only | 3.5 | 0 | 3.5 | 21 | 0 | 21 |  | 35 | 0 | 35
| WMPLSE | 1RU, front/rear, short depth | 2.1 | 6.3 | 8.4 | 12 | 38 | 51 |  | 21 | 64 | 85
| WMPLFSE | 1RU, front only, short depth | 2.1 | 0 | 2.1 | 12 | 0 | 12 |  | 21 | 0 | 21
Note: Rear section may be partially blocked by rack posts
NCMH NetManager™ Horizontal Cable Managers | NCMH2 | 2RU, front/rear | 6 | 8 | 14 | 36 | 48 | 85 |  | 61 | 81 | 142
| NCMHF2 | 2RU, front only | 6 | 0 | 6 | 36 | 0 | 36 |  | 61 | 0 | 61
| NCMHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 14 | 0 | 14 |  | 23 | 0 | 23
NM NetManager™ High Capacity Horizontal Cable Managers | NM1 | 1RU, front/rear | 3.3 | 4.1 | 7.4 | 20 | 25 | 45 |  | 33 | 41 | 75
| NMF1 | 1RU, front only | 3.3 | 0 | 3.3 | 20 | 0 | 20 |  | 33 | 0 | 33
| NM2 | 2RU, front/rear | 9.8 | 11.1 | 20.9 | 59 | 67 | 127 |  | 99 | 113 | 212
| NMF2 | 2RU, front only | 9.8 | 0 | 9.8 | 59 | 0 | 59 |  | 99 | 0 | 99
| NM3 | 3RU, front/rear | 17.3 | 22 | 39.3 | 105 | 134 | 240 |  | 176 | 224 | 400
| NMF3 | 3RU, front only | 17.3 | 0 | 17.3 | 105 | 0 | 105 |  | 176 | 0 | 176
| NM4 | 4RU, front/rear | 24.3 | 31.9 | 56.2 | 148 | 194 | 343 |  | 247 | 324 | 572
| NMF4 | 4RU, front only | 24.3 | 0 | 24.3 | 148 | 0 | 148 |  | 247 | 0 | 247
Note: Rear section may be partially blocked by rack posts
CMPH Open-Access™ Horizontal Cable Managers | CMPH1 | 1RU, front/rear | 2.3 | 2.9 | 5.2 | 14 | 17 | 31 |  | 23 | 29 | 52
| CMPHF1 | 1RU, front only | 2.3 | 0 | 2.3 | 14 | 0 | 14 |  | 23 | 0 | 23
| CMPH2 | 2RU, front/rear | 5.3 | 10.8 | 16.1 | 32 | 66 | 98 |  | 53 | 110 | 163
| CMPHF2 | 2RU, front only | 5.3 | 0 | 5.3 | 32 | 0 | 32 |  | 53 | 0 | 53
| CMPHH2 | 2RU, front only, larger D-rings | 10.8 | 0 | 10.8 | 66 | 0 | 66 |  | 110 | 0 | 110
| CMPHHF1 | 1RU, front only, larger D-rings | 2.9 | 0 | 2.9 | 17 | 0 | 17 |  | 29 | 0 | 29
Note: Rear section may be partially blocked by rack posts
CMVDR Vertical D-rings | CMVDR1 | 5.70"L x 2.00"W |  |  | 6 |  |  | 36 |  |  |  | 61
| CMVDR1S | 3.30"L x 2.00"W |  |  | 3 |  |  | 18 |  |  |  | 30
| CMVDR2 | 5.70"L x 3.00"W |  |  | 10.8 |  |  | 66 |  |  |  | 110
| CMVDR2S | 3.30"L x 3.00"W |  |  | 6 |  |  | 36 |  |  |  | 61
| CMVDRC | between-racks, 5.60"L x 8.00"W |  |  | 24 |  |  | 146 |  |  |  | 244
CM Cable Routing Troughs | CMLT19 | lower trough w/ bend radius |  |  | 22.7 |  |  | 138 |  |  |  | 231
| CMUT19 | upper trough w/ bend radius |  |  | 8.2 |  |  | 50 |  |  |  | 83
| CMT4 | horizontal trough |  |  | 21.9 |  |  | 133 |  |  |  | 223
*Capacity is calculated for within the trough channel only. Higher capacities can be achieved when cables are tied together.
CWMPV IN-Cabinet Vertical Cable Manager | CWMPV2440 | side mount, 2"W x 4"D x 6'H | 5.7 | 0 | 5.7 | 34 | 0 | 34 |  | 58 | 0 | 58
| CWMPV3440 | side mount, 3"W x 4"D x 6'H | 9.1 | 0 | 9.1 | 55 | 0 | 55 |  | 92 | 0 | 92
| CWMPV2340 | side mount, 2"W x 3"D x 6'H | 5.2 | 0 | 5.2 | 31 | 0 | 31 |  | 52 | 0 | 52
| CWMPV3340 | side mount, 3"W x 3"D x 6'H | 7.8 | 0 | 7.8 | 47 | 0 | 47 |  | 79 | 0 | 79
4-Post Rack Vertical Tie-off Panels | V4PTOB | Vertical Tie-off Panel with AR4P 4-Post Racks mount brackets | 31.7 | 0 | 31.7 | 193 | 0 | 193 |  | 322 | 0 | 322
| V4PTOB | Vertical Tie-off Panel with R4P 4-Post Racks mount brackets | 35.8 | 0 | 35.8 | 218 | 0 | 218 |  | 364 | 0 | 364
J-PRO & J-MOD J Hooks | JP75^ | J-Pro™ cable support, 0.75" |  |  | 0.626 |  |  | 5 |  |  |  | 5
| JP131^ | J-Pro™ cable support, 1.31" |  |  | 1.74 |  |  | 14 |  |  |  | 14
| JP2^ | J-Pro™ cable support, 2.0" |  |  | 3.155 |  |  | 25 |  |  |  | 25
| JP4^ | J-Pro™ cable support, 4.0" |  |  | 13.478 |  |  | 109 |  |  |  | 109
| JMJH2^ | J-Mod™ cable support, 2.0" |  |  | 3.037 |  |  | 24 |  |  |  | 24
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
EMT Electrical Metallic Tubing | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 2 |  |  |  | 2
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 4 |  |  |  | 4
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 7 |  |  |  | 7
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 12 |  |  |  | 12
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0367 |  |  | 16 |  |  |  | 16
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 27 |  |  |  | 27
| 2-1/2" | Useable Inside Diameter in inches | 2.731 |  | 5.8601 |  |  | 47 |  |  |  | 47
| 3" | Useable Inside Diameter in inches | 3.356 |  | 8.8493 |  |  | 72 |  |  |  | 72
| 3-1/2" | Useable Inside Diameter in inches | 3.834 |  | 11.5497 |  |  | 94 |  |  |  | 94
| 4" | Useable Inside Diameter in inches | 4.334 |  | 14.7585 |  |  | 120 |  |  |  | 120
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
EMT Electrical Metallic Tubing* | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 2 |  |  |  | 2
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 4 |  |  |  | 4
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 7 |  |  |  | 7
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 12 |  |  |  | 12
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0367 |  |  | 16 |  |  |  | 16
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 27 |  |  |  | 27
| 2-1/2" | Useable Inside Diameter in inches | 2.731 |  | 5.8601 |  |  | 47 |  |  |  | 47
| 3" | Useable Inside Diameter in inches | 3.356 |  | 8.8493 |  |  | 72 |  |  |  | 72
| 3-1/2" | Useable Inside Diameter in inches | 3.834 |  | 11.5497 |  |  | 94 |  |  |  | 94
| 4" | Useable Inside Diameter in inches | 4.334 |  | 14.7585 |  |  | 120 |  |  |  | 120
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
IMC Intermediate Conduit* | 1/2" | Useable Inside Diameter in inches | 0.675 |  | 0.35799 |  |  | 2 |  |  |  | 2
| 3/4" | Useable Inside Diameter in inches | 0.879 |  | 0.60708 |  |  | 4 |  |  |  | 4
| 1" | Useable Inside Diameter in inches | 1.12 |  | 0.9856 |  |  | 8 |  |  |  | 8
| 1-1/4" | Useable Inside Diameter in inches | 1.468 |  | 1.6932 |  |  | 13 |  |  |  | 13
| 1-1/2" | Useable Inside Diameter in inches | 1.703 |  | 2.2787 |  |  | 18 |  |  |  | 18
| 2" | Useable Inside Diameter in inches | 2.17 |  | 3.6998 |  |  | 30 |  |  |  | 30
| 2-1/2" | Useable Inside Diameter in inches | 2.597 |  | 5.2992 |  |  | 43 |  |  |  | 43
| 3" | Useable Inside Diameter in inches | 3.216 |  | 8.1264 |  |  | 66 |  |  |  | 66
| 3-1/2" | Useable Inside Diameter in inches | 3.711 |  | 10.8205 |  |  | 88 |  |  |  | 88
| 4" | Useable Inside Diameter in inches | 4.205 |  | 13.893 |  |  | 113 |  |  |  | 113
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
Rigid Conduit Steel or Aluminum* | 1/2" | Useable Inside Diameter in inches | 0.622 |  | 0.30398 |  |  | 2 |  |  |  | 2
| 3/4" | Useable Inside Diameter in inches | 0.824 |  | 0.53348 |  |  | 4 |  |  |  | 4
| 1" | Useable Inside Diameter in inches | 1.049 |  | 0.8646 |  |  | 7 |  |  |  | 7
| 1-1/4" | Useable Inside Diameter in inches | 1.38 |  | 1.4963 |  |  | 12 |  |  |  | 12
| 1-1/2" | Useable Inside Diameter in inches | 1.61 |  | 2.0367 |  |  | 16 |  |  |  | 16
| 2" | Useable Inside Diameter in inches | 2.067 |  | 3.357 |  |  | 27 |  |  |  | 27
| 2-1/2" | Useable Inside Diameter in inches | 2.469 |  | 4.7897 |  |  | 39 |  |  |  | 39
| 3" | Useable Inside Diameter in inches | 3.068 |  | 7.3956 |  |  | 60 |  |  |  | 60
| 3-1/2" | Useable Inside Diameter in inches | 3.548 |  | 9.8908 |  |  | 80 |  |  |  | 80
| 4" | Useable Inside Diameter in inches | 4.026 |  | 12.7354 |  |  | 103 |  |  |  | 103
| 5" | Useable Inside Diameter in inches | 5.047 |  | 20.0139 |  |  | 163 |  |  |  | 163
| 6" | Useable Inside Diameter in inches | 6.065 |  | 28.9019 |  |  | 235 |  |  |  | 235
*Capacity is calculated for conduit at 40% maximum per NEC guidelines
Cable Capacity Calculator V12

## LEGACY
[7 empty] | Panduit Patch Cord Approximate Diameters | [5 empty] | Cat 6A Plenum UTP Cable | Dia. (in.)
[13 empty] | Panduit Vari-MaTriX HD | 0.23
[7 empty] | Cat. | AWG | in. |  | mm |  | Panduit Std Comp+ HD | 0.23
[7 empty] | 5e | 28 | 0.149 |  | 3.7846 |  | CommScope 2091B | 0.285
[7 empty] | 5e | 24 | 0.215 |  | 5.461 |  | CommScope 2091SD | 0.265
[7 empty] | 6 | 28 | 0.15 |  | 3.81 |  | Belden 10GXS | 0.265
Enter the cable diameter below and select in. or mm. | [6 empty] | 6 | 24 | 0.235 |  | 5.969 |  | Berk-Tek LANmark-XTP | 0.275
[7 empty] | 6A | 28 | 0.185 |  | 4.699
Cable Diameter = | 0.3 | 1 |  |  |  |  | 6A | 24 | 0.25 |  | 6.35
| Duplex Cable? | 1
Product Family | Part Number | Description | Cable Manager Area |  |  | Recommended Cable Fill (30%) |  |  |  | Maximum Cable Fill (50%)
|  |  | Front Usable Area (sq. in.) | Rear Usable Area (sq. in.) | Total Usable Area (sq. in.) | Front | Rear | Total |  | Front | Rear | Total
NRV NetRunner™ High Capacity Vertical Cable Managers | NRV10 | 10" wide, 45RU | 49.1 | 49.1 | 98.2 | 208 | 208 | 416 |  | 347 | 347 | 694
| NRVF10 | 10" wide, 45RU, front only | 49.1 | 0 | 49.1 | 208 | 0 | 208 |  | 347 | 0 | 347
| Single NRV Finger |  |  |  | 4.7 | 19 |  |  |  | 33
PEHF PatchRunner™ High Capacity Horizontal Cable Managers | PEHF2 | 2RU, front only | 16.6 | 0 | 16.6 | 70 | 0 | 70 |  | 117 | 0 | 117
| PEHF3 | 3RU, front only | 29.6 | 0 | 29.6 | 125 | 0 | 125 |  | 209 | 0 | 209
| PEHF4 | 4RU, front only | 42.8 | 0 | 42.8 | 181 | 0 | 181 |  | 302 | 0 | 302
CWMPV IN-Cabinet Vertical Cable Manager | CWMPV2418 | side mount, 2"W x 4"D x 2.6'H | 5.7 | 0 | 5.7 | 24 | 0 | 24 |  | 40 | 0 | 40
| CWMPV3418 | side mount, 3"W x 4"D x 2.6'H | 9.1 | 0 | 9.1 | 38 | 0 | 38 |  | 64 | 0 | 64
| CWMPV2318 | side mount, 2"W x 3"D x 2.6'H | 5.2 | 0 | 5.2 | 22 | 0 | 22 |  | 36 | 0 | 36
| CWMPV3318 | side mount, 3"W x 3"D x 2.6'H | 7.8 | 0 | 7.8 | 33 | 0 | 33 |  | 55 | 0 | 55
*Capacity is calculated for J Hooks with a 50% recommended fill and 70% maximum fill.
Cable Capacity Calculator V12

## numbers (hidden)
in. | no
mm | yes
30% | 40%
50% | 40%
0.215 | 0.185 | 0.275 | 0.15 | 0.235